## Sheet1
Process | Flocculation Time minimum (min) | Flocculation Time maximum (min) | Clarification Component loading rate minimum (gpm/ft2) | Clarification Component loading rate maximum (gpm/ft2) | Sludge Volume minimum (%) | Sludge Volume maximum (%) | Solids Concentration minimum (% by weight) | Solids Concentration maximum (% by weight) | Energy minimum (includes 1.25 hp for rapid mix) hp/mgd | Energy maximum (includes 1.25 hp for rapid mix) hp/mgd | Relative equipment cost | Detention time (min) (has Direct impact on construction cost) | Advantages | Disadvantages
Conventional | 20 | 45 | 0.3 | 0.5 | 2 | 4 | 0.25 | 0.5 | 1.5 | 2 | Minimal | 240 | ▪ Robust, well proven ▪ Low Operation Cost ▪ Ability to incorporate PAC | ▪ Large footprint ▪ Not suitable for light solids ▪ Low solids content ▪ Some temperature effects
Plate Settlers | 20 | 45 | 4 | 8 | 2 | 4 | 0.25 | 0.5 | 1.5 | 2 | Medium | 60 | ▪ Robust, well proven ▪ Small footprint ▪ Low operating cost | ▪ Not suitable for light solids ▪ Low solids content ▪ Some temperature effects ▪ May not have sufficient time for PAC
Actiflo® | 5 | 10 | 16 | 35 | 3 | 6 | 0.1 | 0.4 | 2 | 4 | High | 15 | ▪ Smallest footprint ▪ High quality water ▪ Quick startup and optimization ▪ Reduced chemical consumption | ▪ Polymer and sand grit carryover ▪ Short detention time with PAC ▪ Low solids content ▪ High operating costs
DAF (conventional) sludge scraper | 10 | 20 | 4 | 6 | 1 | 1 | 2 | 4 | 4 | 4 | Medium High | 50 | ▪ Small footprint ▪ Ideal for light solids ▪ Low chemical consumption | ▪ Not suitable for high dense solids ▪ Turbidity limitations ▪ High operating cost ▪ May need polymer
DAF (high rate) sludge scraper | 10 | 20 | 6 | 15 | 1 | 1 | 2 | 4 | 4 | 4 | Medium High | 20 | ▪ Small footprint ▪ Ideal for light solids ▪ Low chemical consumption | ▪ Not suitable for high dense solids ▪ Turbidity limitations ▪ High operating cost ▪ May need polymer
Superpulsator® | 1 | 1 | 2 | 5 | 0.5 | 2 | 0.2 | 0.3 | 2 | 2.5 | Low | 60 | ▪ Ability to incorporate PAC ▪ No moving parts ▪ No separate flocculation ▪ Performs well at cold temperatures ▪ Requires polymer for high rate sed | ▪ Poor performance during rapid temperature changes ▪ Best with denser floc ▪ Flow and water quality variations
DensaDeg® | 8 | 10 | 8 | 10 | 1 | 1 | 2 | 4 | 2 | 3 | Medium High | 30 | ▪ Ability to hold PAC ▪ Small footprint ▪ High solids content | ▪ Polymer carryover
AguaClara | 1 | 10 | 1.5 | 1.5 |  |  |  |  | 0 | 0 | Ultra Low | 30